## Arkusz1
Mapa MODBUS
28.09.2020			Opis kodu i problemow sterownaia czlonami pasywnymi
pre		Bartosz Ostrowski	na podstawie dok. z 28-09-2020 Opisy kodu i problemow …
9.10.2020		Piotr Romaniuk	aktualziacja na podstawie zrodel i planowanych zmian (dyskutowane)
~21-10	v1.02	Tomasz Święchowicz	wstawienie tangens_range w holding-registers; rozbicie control_bits na dwa rejestry
5.11.2020		Piotr Romaniuk	usunięcie wyroznienia ostatnich zmian

Opis mapy został przeniesiony do plików modbus_map.txt
Ten plik nie będzie już używany

Input_registers

konwencja oznaczen
		a, b, c, n	= L1, L2, L3, N
		A, B	'= upper Q, bottom Q (pwm)
jednostki
		temperatura	[*C]
		napiecia i prady	[V] i [A]
		moc czynna	[W]
		moc bierna	[var]
		moc pozorna	[VA]
typy danych
	temperatura	i16	[*C]

	3F coefficients	float[ 3 ]	kolejne składowe a, b, c odpowiadajace L1, L2, L3
	3FN	float[ 4 ]	jw + N
				prze MODBUS:
	u32	u16 L	L, H – big endian u16	[c d]
		u16 H	u32 = [ a b c d ]	[a b]
	float	u16 Lfloat	analogia do u32	[ c d ]
		u16 Hfloat	float = [a b c d]	[a b ]

	TIME	u16[3]	BCD kodowanie
		2	YY MM	YY – offset ponad 2000
		1	DD HH
		0	mm SS

0-127		FatFS_response	bufor 128 rejstrow
128	Alarm_0	bit			alarmy skumulowane
		0x0001	I_conv_a_H	:1;	a, b, c, n = {L1, L2, L3, N}?
		0x0002	I_conv_a_L	:1;	H – przekroczenie max, L – przekroczenie min
		0x0004	I_conv_b_H	:1;
		0x0008	I_conv_b_L	:1;
		0x0010	I_conv_c_H	:1;
		0x0020	I_conv_c_L	:1;
		0x0040	I_conv_n_H	:1;
		0x0080	I_conv_n_L	:1;
		0x0100	I_conv_a_SDH	:1;	SD – blad komparatora
		0x0200	I_conv_a_SDL	:1;
		0x0400	I_conv_b_SDH	:1;
		0x0800	I_conv_b_SDL	:1;
		0x1000	I_conv_c_SDH	:1;
		0x2000	I_conv_c_SDL	:1;
		0x4000	I_conv_n_SDH	:1;
		0x8000	I_conv_n_SDL	:1;

129	Alarm_1
		0x0001	Temperature_H	:1;
		0x0002	Temperature_L	:1;
		0x0004	U_dc_H	:1;
		0x0008	U_dc_L	:1;
		0x0010	Driver_PWM_a_A	1;	driver a-n = {L1,L2,L3,N) - A, B – gora/dol
		0x0020	Driver_PWM_a_B	1;
		0x0040	Driver_PWM_b_A	1;
		0x0080	Driver_PWM_b_B	1;
		0x0100	Driver_PWM_c_A	1;
		0x0200	Driver_PWM_c_B	1;
		0x0400	Driver_PWM_n_A	1;
		0x0800	Driver_PWM_n_B	1;
		0x1000	No_calibration	1;
		0x2000	CT_char_error	1;
		0x4000	PLL_UNSYNC	1;
		0x8000	CONV_SOFTSTART	1;

130	Alarm_2
		0x0001	FUSE_BROKEN	1;
		0x0002	TZ_FLT_SUPPLY	1;
		0x0004	TZ_DRV_FLT	1;
		0x0008	TZ_CLOCKFAIL	1;
		0x0010	TZ_EMUSTOP	1;
		0x0020	TZ_SD_COMP	1;
		0x0040	TZ	1;
		0x0080	I_conv_rms_a	1;
		0x0100	I_conv_rms_b	1;
		0x0200	I_conv_rms_c	1;
		0x0400	I_conv_rms_n	1;
		0x0800	U_grid_rms_a_L	1;
		0x1000	U_grid_rms_b_L	1;
		0x2000	U_grid_rms_c_L	1;
		0x4000	U_grid_abs_a_H	1;
		0x8000	U_grid_abs_b_H	1;

131	Alarm_3	0x0001	U_grid_abs_c_H	1;
		0x0002		1;
		0x0004		1;
		0x0008		1;
		0x0010		1;
		0x0020		1;
		0x0040		1;
		0x0080		1;
		0x0100		1;
		0x0200		1;
		0x0400		1;
		0x0800		1;
		0x1000		1;
		0x2000		1;
		0x4000		1;
		0x8000		1;

132		Alarm_0_snapshot		co spowodowalo zatrzymanie
133		Alarm_1_snapshot
134		Alarm_2_snapshot
135		Alarm_3_snapshot

136		STATUS_0
		0x0001	Init_done	:1;
		0x0002	ONOFF	:1;
		0x0004	DS1_switch_SD_CT	:1;
		0x0008	DS2_enable_Q_comp	:1;
		0x0010	DS3_enable_P_sym	:1;
		0x0020	DS4_enable_H_comp	:1;
		0x0040	DS5_limit_to_9odd_harmonics	:1;
		0x0080	DS6_limit_to_14odd_harmonics	:1;
		0x0100	DS7_limit_to_19odd_harmonics	:1;
		0x0200	DS8_DS_override	:1;
		0x0400	calibration_procedure_error	:1;
		0x0800	L_grid_measured	:1;
		0x1000	Scope_snapshot_pending	:1;
		0x2000	Scope_snapshot_error	:1;
		0x4000	SD_card_not_enough_data	:1;
		0x8000	SD_no_CT_characteristic	:	1;

137		STATUS_1
		0x0001	SD_no_calibration	:	1;
		0x0002	SD_no_harmonic_settings	:	1;
		0x0004	SD_no_settings	:	1;
		0x0008	FLASH_not_enough_data	:	1;
		0x0010	FLASH_no_CT_characteristic	:	1;
		0x0020	FLASH_no_calibration	:	1;
		0x0040	FLASH_no_harmonic_settings	:	1;
		0x0080	FLASH_no_settings	:	1;
		0x0100	in_limit_Q	:	1;
		0x0200	in_limit_P	:	1;
		0x0400	in_limit_H	:	1;
		0x0800	Conv_active	:	1;
		0x1000	PLL_sync	:	1;
		0x2000	Grid_present	:	1;
		0x4000	rsvd	:	1;
		0x8000	rsvd	:	1;

138		STATUS_2	rsvd	:	16
139		STATUS_3	rsvd	:	16

140		Machine_state_0		po co enum u32? CLA ma typy
			Machine_init,
			Machine_calibrate_offsets,
			Machine_calibrate_curent_gain,
			Machine_calibrate_AC_voltage_gain,
			Machine_calibrate_DC_voltage_gain,
			Machine_idle,
			Machine_start,
			Machine_Lgrid_meas,
			Machine_operational,
			Machine_cleanup,
			Machine_cleanup_delay,
			__dummybig_Machine = 300000	493E0

141		Machine_state_1
142		Converter_state_0
			CONV_softstart,
			CONV_grid_relay,
			CONV_active,
			__dummybig_CONV = 300000

143		Converter_state_1
144		float-> i16	Temp1
145			Temp2
146			Temp3
147			Temp_CPU
148		float	L_grid_previous_0
149
150			L_grid_previous_1
151
152			L_grid_previous_2

154			L_grid_previous_3

156			L_grid_previous_4

158			L_grid_previous_5

160			L_grid_previous_6

162			L_grid_previous_7

164			L_grid_previous_8

166			L_grid_previous_9

168			file_head
169		TIME	RTC_current_time

172		rsvd

255		rsvd
256	3F coefficients	L1_I_grid_1h_float_L
257		L1_I_grid_1h_float_H
258		L2_I_grid_1h_float_L
259		L2_I_grid_1h_float_H
260		L3_I_grid_1h_float_L
261		L3_I_grid_1h_float_H
262	3F coefficients	L1_U_grid_1h_float_L
263		L1_U_grid_1h_float_H
264		L2_U_grid_1h_float_L
265		L2_U_grid_1h_float_H
266		L3_U_grid_1h_float_L
267		L3_U_grid_1h_float_H
268	3F coefficients	L1_P_grid_1h_float_L
269		L1_P_grid_1h_float_H
270		L2_P_grid_1h_float_L
271		L2_P_grid_1h_float_H
272		L3_P_grid_1h_float_L
273		L3_P_grid_1h_float_H
274	3F coefficients	L1_P_load_1h_float_L
275		L1_P_load_1h_float_H
276		L2_P_load_1h_float_L
277		L2_P_load_1h_float_H
278		L3_P_load_1h_float_L
279		L3_P_load_1h_float_H
280	3F coefficients	L1_P_conv_1h_float_L
281		L1_P_conv_1h_float_H
282		L2_P_conv_1h_float_L
283		L2_P_conv_1h_float_H
284		L3_P_conv_1h_float_L
285		L3_P_conv_1h_float_H
286	3F coefficients	L1_Q_grid_1h_float_L
287		L1_Q_grid_1h_float_H
288		L2_Q_grid_1h_float_L
289		L2_Q_grid_1h_float_H
290		L3_Q_grid_1h_float_L
291		L3_Q_grid_1h_float_H
292	3F coefficients	L1_Q_load_1h_float_L
293		L1_Q_load_1h_float_H
294		L2_Q_load_1h_float_L
295		L2_Q_load_1h_float_H
296		L3_Q_load_1h_float_L
297		L3_Q_load_1h_float_H
298	3F coefficients	L1_Q_conv_1h_float_L
299		L1_Q_conv_1h_float_H
300		L2_Q_conv_1h_float_L
301		L2_Q_conv_1h_float_H
302		L3_Q_conv_1h_float_L
303		L3_Q_conv_1h_float_H
304	3F coefficients	L1_S_grid_1h_float_L
305		L1_S_grid_1h_float_H
306		L2_S_grid_1h_float_L
307		L2_S_grid_1h_float_H
308		L3_S_grid_1h_float_L
309		L3_S_grid_1h_float_H
310	3F coefficients	L1_S_load_1h_float_L
311		L1_S_load_1h_float_H
312		L2_S_load_1h_float_L
313		L2_S_load_1h_float_H
314		L3_S_load_1h_float_L
315		L3_S_load_1h_float_H
316	3F coefficients	L1_S_conv_1h_float_L
317		L1_S_conv_1h_float_H
318		L2_S_conv_1h_float_L
319		L2_S_conv_1h_float_H
320		L3_S_conv_1h_float_L
321		L3_S_conv_1h_float_H
322	3F coefficients	L1_PF_grid_1h_float_L
323		L1_PF_grid_1h_float_H
324		L2_PF_grid_1h_float_L
325		L2_PF_grid_1h_float_H
326		L3_PF_grid_1h_float_L
327		L3_PF_grid_1h_float_H
328	3F coefficients	L1_THD_I_grid_float_L
329		L1_THD_I_grid_float_H
330		L2_THD_I_grid_float_L
331		L2_THD_I_grid_float_H
332		L3_THD_I_grid_float_L
333		L3_THD_I_grid_float_H
334	3F coefficients	L1_THD_U_grid_float_L
335		L1_THD_U_grid_float_H
336		L2_THD_U_grid_float_L
337		L2_THD_U_grid_float_H
338		L3_THD_U_grid_float_L
339		L3_THD_U_grid_float_H
340	3F coefficients	L1_U_grid_float_L
341		L1_U_grid_float_H
342		L2_U_grid_float_L
343		L2_U_grid_float_H
344		L3_U_grid_float_L
345		L3_U_grid_float_H
346	3F coefficients	L1_I_grid_float_L
347		L1_I_grid_float_H
348		L2_I_grid_float_L
349		L2_I_grid_float_H
350		L3_I_grid_float_L
351		L3_I_grid_float_H
352	3FN coefficients	L1_I_conv_float_L
353		L1_I_conv_float_H
354		L2_I_conv_float_L
355		L2_I_conv_float_H
356		L3_I_conv_float_L
357		L3_I_conv_float_H
358		N_I_conv_float_L
359		N_I_conv_float_H
360	3F coefficients	L1_S_grid_float_L
361		L1_S_grid_float_H
362		L2_S_grid_float_L
363		L2_S_grid_float_H
364		L3_S_grid_float_L
365		L3_S_grid_float_H
366	3F coefficients	L1_S_conv_float_L
367		L1_S_conv_float_H
368		L2_S_conv_float_L
369		L2_S_conv_float_H
370		L3_S_conv_float_L
371		L3_S_conv_float_H
372	3FN coefficients	L1_Used_resources_float_L
373		L1_Used_resources_float_H
374		L2_Used_resources_float_L
375		L2_Used_resources_float_H
376		L3_Used_resources_float_L
377		L3_Used_resources_float_H
378		N_Used_resources_float_L
379		N_Used_resources_float_H
380	float	PF_grid_1h_float_L
381		PF_grid_1h_float_H
382	float	P_load_1h_float_L
383		P_load_1h_float_H
384	float	Q_load_1h_float_L
385		Q_load_1h_float_H
386	float	S_load_1h_float_L
387		S_load_1h_float_H
388	float	P_grid_1h_float_L
389		P_grid_1h_float_H
390	float	Q_grid_1h_float_L
391		Q_grid_1h_float_H
392	float	S_grid_1h_float_L
393		S_grid_1h_float_H
394	float	U_grid_1h_float_L
395		U_grid_1h_float_H
396	float	frequency_float_L
397		frequency_float_H
398		rsvd
...
511		rsvd
512	float	I_grid_L1_harmonic_amplitudes_00_L
513		I_grid_L1_harmonic_amplitudes_00_H
514	float	I_grid_L1_harmonic_amplitudes_01_L
515		I_grid_L1_harmonic_amplitudes_01_H
516	float	I_grid_L1_harmonic_amplitudes_02_L
517		I_grid_L1_harmonic_amplitudes_02_H
518	float	I_grid_L1_harmonic_amplitudes_03_L
519		I_grid_L1_harmonic_amplitudes_03_H
520	float	I_grid_L1_harmonic_amplitudes_04_L
521		I_grid_L1_harmonic_amplitudes_04_H
522	float	I_grid_L1_harmonic_amplitudes_05_L
523		I_grid_L1_harmonic_amplitudes_05_H
524	float	I_grid_L1_harmonic_amplitudes_06_L
525		I_grid_L1_harmonic_amplitudes_06_H
526	float	I_grid_L1_harmonic_amplitudes_07_L
527		I_grid_L1_harmonic_amplitudes_07_H
528	float	I_grid_L1_harmonic_amplitudes_08_L
529		I_grid_L1_harmonic_amplitudes_08_H
530	float	I_grid_L1_harmonic_amplitudes_09_L
531		I_grid_L1_harmonic_amplitudes_09_H
532	float	I_grid_L1_harmonic_amplitudes_10_L
533		I_grid_L1_harmonic_amplitudes_10_H
534	float	I_grid_L1_harmonic_amplitudes_11_L
535		I_grid_L1_harmonic_amplitudes_11_H
536	float	I_grid_L1_harmonic_amplitudes_12_L
537		I_grid_L1_harmonic_amplitudes_12_H
538	float	I_grid_L1_harmonic_amplitudes_13_L
539		I_grid_L1_harmonic_amplitudes_13_H
540	float	I_grid_L1_harmonic_amplitudes_14_L
541		I_grid_L1_harmonic_amplitudes_14_H
542	float	I_grid_L1_harmonic_amplitudes_15_L
543		I_grid_L1_harmonic_amplitudes_15_H
544	float	I_grid_L1_harmonic_amplitudes_16_L
545		I_grid_L1_harmonic_amplitudes_16_H
546	float	I_grid_L1_harmonic_amplitudes_17_L
547		I_grid_L1_harmonic_amplitudes_17_H
548	float	I_grid_L1_harmonic_amplitudes_18_L
549		I_grid_L1_harmonic_amplitudes_18_H
550	float	I_grid_L1_harmonic_amplitudes_19_L
551		I_grid_L1_harmonic_amplitudes_19_H
552	float	I_grid_L1_harmonic_amplitudes_20_L
553		I_grid_L1_harmonic_amplitudes_20_H
554	float	I_grid_L1_harmonic_amplitudes_21_L
555		I_grid_L1_harmonic_amplitudes_21_H
556	float	I_grid_L1_harmonic_amplitudes_22_L
557		I_grid_L1_harmonic_amplitudes_22_H
558	float	I_grid_L1_harmonic_amplitudes_23_L
559		I_grid_L1_harmonic_amplitudes_23_H
560	float	I_grid_L1_harmonic_amplitudes_24_L
561		I_grid_L1_harmonic_amplitudes_24_H
562	float	I_grid_L1_harmonic_amplitudes_25_L
563		I_grid_L1_harmonic_amplitudes_25_H
564	float	I_grid_L2_harmonic_amplitudes_00_L
565		I_grid_L2_harmonic_amplitudes_00_H
566	float	I_grid_L2_harmonic_amplitudes_01_L
567		I_grid_L2_harmonic_amplitudes_01_H
568	float	I_grid_L2_harmonic_amplitudes_02_L
569		I_grid_L2_harmonic_amplitudes_02_H
570	float	I_grid_L2_harmonic_amplitudes_03_L
571		I_grid_L2_harmonic_amplitudes_03_H
572	float	I_grid_L2_harmonic_amplitudes_04_L
573		I_grid_L2_harmonic_amplitudes_04_H
574	float	I_grid_L2_harmonic_amplitudes_05_L
575		I_grid_L2_harmonic_amplitudes_05_H
576	float	I_grid_L2_harmonic_amplitudes_06_L
577		I_grid_L2_harmonic_amplitudes_06_H
578	float	I_grid_L2_harmonic_amplitudes_07_L
579		I_grid_L2_harmonic_amplitudes_07_H
580	float	I_grid_L2_harmonic_amplitudes_08_L
581		I_grid_L2_harmonic_amplitudes_08_H
582	float	I_grid_L2_harmonic_amplitudes_09_L
583		I_grid_L2_harmonic_amplitudes_09_H
584	float	I_grid_L2_harmonic_amplitudes_10_L
585		I_grid_L2_harmonic_amplitudes_10_H
586	float	I_grid_L2_harmonic_amplitudes_11_L
587		I_grid_L2_harmonic_amplitudes_11_H
588	float	I_grid_L2_harmonic_amplitudes_12_L
589		I_grid_L2_harmonic_amplitudes_12_H
590	float	I_grid_L2_harmonic_amplitudes_13_L
591		I_grid_L2_harmonic_amplitudes_13_H
592	float	I_grid_L2_harmonic_amplitudes_14_L
593		I_grid_L2_harmonic_amplitudes_14_H
594	float	I_grid_L2_harmonic_amplitudes_15_L
595		I_grid_L2_harmonic_amplitudes_15_H
596	float	I_grid_L2_harmonic_amplitudes_16_L
597		I_grid_L2_harmonic_amplitudes_16_H
598	float	I_grid_L2_harmonic_amplitudes_17_L
599		I_grid_L2_harmonic_amplitudes_17_H
600	float	I_grid_L2_harmonic_amplitudes_18_L
601		I_grid_L2_harmonic_amplitudes_18_H
602	float	I_grid_L2_harmonic_amplitudes_19_L
603		I_grid_L2_harmonic_amplitudes_19_H
604	float	I_grid_L2_harmonic_amplitudes_20_L
605		I_grid_L2_harmonic_amplitudes_20_H
606	float	I_grid_L2_harmonic_amplitudes_21_L
607		I_grid_L2_harmonic_amplitudes_21_H
608	float	I_grid_L2_harmonic_amplitudes_22_L
609		I_grid_L2_harmonic_amplitudes_22_H
610	float	I_grid_L2_harmonic_amplitudes_23_L
611		I_grid_L2_harmonic_amplitudes_23_H
612	float	I_grid_L2_harmonic_amplitudes_24_L
613		I_grid_L2_harmonic_amplitudes_24_H
614	float	I_grid_L2_harmonic_amplitudes_25_L
615		I_grid_L2_harmonic_amplitudes_25_H
616	float	I_grid_L3_harmonic_amplitudes_00_L
617		I_grid_L3_harmonic_amplitudes_00_H
618	float	I_grid_L3_harmonic_amplitudes_01_L
619		I_grid_L3_harmonic_amplitudes_01_H
620	float	I_grid_L3_harmonic_amplitudes_02_L
621		I_grid_L3_harmonic_amplitudes_02_H
622	float	I_grid_L3_harmonic_amplitudes_03_L
623		I_grid_L3_harmonic_amplitudes_03_H
624	float	I_grid_L3_harmonic_amplitudes_04_L
625		I_grid_L3_harmonic_amplitudes_04_H
626	float	I_grid_L3_harmonic_amplitudes_05_L
627		I_grid_L3_harmonic_amplitudes_05_H
628	float	I_grid_L3_harmonic_amplitudes_06_L
629		I_grid_L3_harmonic_amplitudes_06_H
630	float	I_grid_L3_harmonic_amplitudes_07_L
631		I_grid_L3_harmonic_amplitudes_07_H
632	float	I_grid_L3_harmonic_amplitudes_08_L
633		I_grid_L3_harmonic_amplitudes_08_H
634	float	I_grid_L3_harmonic_amplitudes_09_L
635		I_grid_L3_harmonic_amplitudes_09_H
636	float	I_grid_L3_harmonic_amplitudes_10_L
637		I_grid_L3_harmonic_amplitudes_10_H
638	float	I_grid_L3_harmonic_amplitudes_11_L
639		I_grid_L3_harmonic_amplitudes_11_H
640	float	I_grid_L3_harmonic_amplitudes_12_L
641		I_grid_L3_harmonic_amplitudes_12_H
642	float	I_grid_L3_harmonic_amplitudes_13_L
643		I_grid_L3_harmonic_amplitudes_13_H
644	float	I_grid_L3_harmonic_amplitudes_14_L
645		I_grid_L3_harmonic_amplitudes_14_H
646	float	I_grid_L3_harmonic_amplitudes_15_L
647		I_grid_L3_harmonic_amplitudes_15_H
648	float	I_grid_L3_harmonic_amplitudes_16_L
649		I_grid_L3_harmonic_amplitudes_16_H
650	float	I_grid_L3_harmonic_amplitudes_17_L
651		I_grid_L3_harmonic_amplitudes_17_H
652	float	I_grid_L3_harmonic_amplitudes_18_L
653		I_grid_L3_harmonic_amplitudes_18_H
654	float	I_grid_L3_harmonic_amplitudes_19_L
655		I_grid_L3_harmonic_amplitudes_19_H
656	float	I_grid_L3_harmonic_amplitudes_20_L
657		I_grid_L3_harmonic_amplitudes_20_H
658	float	I_grid_L3_harmonic_amplitudes_21_L
659		I_grid_L3_harmonic_amplitudes_21_H
660	float	I_grid_L3_harmonic_amplitudes_22_L
661		I_grid_L3_harmonic_amplitudes_22_H
662	float	I_grid_L3_harmonic_amplitudes_23_L
663		I_grid_L3_harmonic_amplitudes_23_H
664	float	I_grid_L3_harmonic_amplitudes_24_L
665		I_grid_L3_harmonic_amplitudes_24_H
666	float	I_grid_L3_harmonic_amplitudes_25_L
667		I_grid_L3_harmonic_amplitudes_25_H
668	float	U_grid_L1_harmonic_amplitudes_00_L
669		U_grid_L1_harmonic_amplitudes_00_H
670	float	U_grid_L1_harmonic_amplitudes_01_L
671		U_grid_L1_harmonic_amplitudes_01_H
672	float	U_grid_L1_harmonic_amplitudes_02_L
673		U_grid_L1_harmonic_amplitudes_02_H
674	float	U_grid_L1_harmonic_amplitudes_03_L
675		U_grid_L1_harmonic_amplitudes_03_H
676	float	U_grid_L1_harmonic_amplitudes_04_L
677		U_grid_L1_harmonic_amplitudes_04_H
678	float	U_grid_L1_harmonic_amplitudes_05_L
679		U_grid_L1_harmonic_amplitudes_05_H
680	float	U_grid_L1_harmonic_amplitudes_06_L
681		U_grid_L1_harmonic_amplitudes_06_H
682	float	U_grid_L1_harmonic_amplitudes_07_L
683		U_grid_L1_harmonic_amplitudes_07_H
684	float	U_grid_L1_harmonic_amplitudes_08_L
685		U_grid_L1_harmonic_amplitudes_08_H
686	float	U_grid_L1_harmonic_amplitudes_09_L
687		U_grid_L1_harmonic_amplitudes_09_H
688	float	U_grid_L1_harmonic_amplitudes_10_L
689		U_grid_L1_harmonic_amplitudes_10_H
690	float	U_grid_L1_harmonic_amplitudes_11_L
691		U_grid_L1_harmonic_amplitudes_11_H
692	float	U_grid_L1_harmonic_amplitudes_12_L
693		U_grid_L1_harmonic_amplitudes_12_H
694	float	U_grid_L1_harmonic_amplitudes_13_L
695		U_grid_L1_harmonic_amplitudes_13_H
696	float	U_grid_L1_harmonic_amplitudes_14_L
697		U_grid_L1_harmonic_amplitudes_14_H
698	float	U_grid_L1_harmonic_amplitudes_15_L
699		U_grid_L1_harmonic_amplitudes_15_H
700	float	U_grid_L1_harmonic_amplitudes_16_L
701		U_grid_L1_harmonic_amplitudes_16_H
702	float	U_grid_L1_harmonic_amplitudes_17_L
703		U_grid_L1_harmonic_amplitudes_17_H
704	float	U_grid_L1_harmonic_amplitudes_18_L
705		U_grid_L1_harmonic_amplitudes_18_H
706	float	U_grid_L1_harmonic_amplitudes_19_L
707		U_grid_L1_harmonic_amplitudes_19_H
708	float	U_grid_L1_harmonic_amplitudes_20_L
709		U_grid_L1_harmonic_amplitudes_20_H
710	float	U_grid_L1_harmonic_amplitudes_21_L
711		U_grid_L1_harmonic_amplitudes_21_H
712	float	U_grid_L1_harmonic_amplitudes_22_L
713		U_grid_L1_harmonic_amplitudes_22_H
714	float	U_grid_L1_harmonic_amplitudes_23_L
715		U_grid_L1_harmonic_amplitudes_23_H
716	float	U_grid_L1_harmonic_amplitudes_24_L
717		U_grid_L1_harmonic_amplitudes_24_H
718	float	U_grid_L1_harmonic_amplitudes_25_L
719		U_grid_L1_harmonic_amplitudes_25_H
720	float	U_grid_L2_harmonic_amplitudes_00_L
721		U_grid_L2_harmonic_amplitudes_00_H
722	float	U_grid_L2_harmonic_amplitudes_01_L
723		U_grid_L2_harmonic_amplitudes_01_H
724	float	U_grid_L2_harmonic_amplitudes_02_L
725		U_grid_L2_harmonic_amplitudes_02_H
726	float	U_grid_L2_harmonic_amplitudes_03_L
727		U_grid_L2_harmonic_amplitudes_03_H
728	float	U_grid_L2_harmonic_amplitudes_04_L
729		U_grid_L2_harmonic_amplitudes_04_H
730	float	U_grid_L2_harmonic_amplitudes_05_L
731		U_grid_L2_harmonic_amplitudes_05_H
732	float	U_grid_L2_harmonic_amplitudes_06_L
733		U_grid_L2_harmonic_amplitudes_06_H
734	float	U_grid_L2_harmonic_amplitudes_07_L
735		U_grid_L2_harmonic_amplitudes_07_H
736	float	U_grid_L2_harmonic_amplitudes_08_L
737		U_grid_L2_harmonic_amplitudes_08_H
738	float	U_grid_L2_harmonic_amplitudes_09_L
739		U_grid_L2_harmonic_amplitudes_09_H
740	float	U_grid_L2_harmonic_amplitudes_10_L
741		U_grid_L2_harmonic_amplitudes_10_H
742	float	U_grid_L2_harmonic_amplitudes_11_L
743		U_grid_L2_harmonic_amplitudes_11_H
744	float	U_grid_L2_harmonic_amplitudes_12_L
745		U_grid_L2_harmonic_amplitudes_12_H
746	float	U_grid_L2_harmonic_amplitudes_13_L
747		U_grid_L2_harmonic_amplitudes_13_H
748	float	U_grid_L2_harmonic_amplitudes_14_L
749		U_grid_L2_harmonic_amplitudes_14_H
750	float	U_grid_L2_harmonic_amplitudes_15_L
751		U_grid_L2_harmonic_amplitudes_15_H
752	float	U_grid_L2_harmonic_amplitudes_16_L
753		U_grid_L2_harmonic_amplitudes_16_H
754	float	U_grid_L2_harmonic_amplitudes_17_L
755		U_grid_L2_harmonic_amplitudes_17_H
756	float	U_grid_L2_harmonic_amplitudes_18_L
757		U_grid_L2_harmonic_amplitudes_18_H
758	float	U_grid_L2_harmonic_amplitudes_19_L
759		U_grid_L2_harmonic_amplitudes_19_H
760	float	U_grid_L2_harmonic_amplitudes_20_L
761		U_grid_L2_harmonic_amplitudes_20_H
762	float	U_grid_L2_harmonic_amplitudes_21_L
763		U_grid_L2_harmonic_amplitudes_21_H
764	float	U_grid_L2_harmonic_amplitudes_22_L
765		U_grid_L2_harmonic_amplitudes_22_H
766	float	U_grid_L2_harmonic_amplitudes_23_L
767		U_grid_L2_harmonic_amplitudes_23_H
768	float	U_grid_L2_harmonic_amplitudes_24_L
769		U_grid_L2_harmonic_amplitudes_24_H
770	float	U_grid_L2_harmonic_amplitudes_25_L
771		U_grid_L2_harmonic_amplitudes_25_H
772	float	U_grid_L3_harmonic_amplitudes_00_L
773		U_grid_L3_harmonic_amplitudes_00_H
774	float	U_grid_L3_harmonic_amplitudes_01_L
775		U_grid_L3_harmonic_amplitudes_01_H
776	float	U_grid_L3_harmonic_amplitudes_02_L
777		U_grid_L3_harmonic_amplitudes_02_H
778	float	U_grid_L3_harmonic_amplitudes_03_L
779		U_grid_L3_harmonic_amplitudes_03_H
780	float	U_grid_L3_harmonic_amplitudes_04_L
781		U_grid_L3_harmonic_amplitudes_04_H
782	float	U_grid_L3_harmonic_amplitudes_05_L
783		U_grid_L3_harmonic_amplitudes_05_H
784	float	U_grid_L3_harmonic_amplitudes_06_L
785		U_grid_L3_harmonic_amplitudes_06_H
786	float	U_grid_L3_harmonic_amplitudes_07_L
787		U_grid_L3_harmonic_amplitudes_07_H
788	float	U_grid_L3_harmonic_amplitudes_08_L
789		U_grid_L3_harmonic_amplitudes_08_H
790	float	U_grid_L3_harmonic_amplitudes_09_L
791		U_grid_L3_harmonic_amplitudes_09_H
792	float	U_grid_L3_harmonic_amplitudes_10_L
793		U_grid_L3_harmonic_amplitudes_10_H
794	float	U_grid_L3_harmonic_amplitudes_11_L
795		U_grid_L3_harmonic_amplitudes_11_H
796	float	U_grid_L3_harmonic_amplitudes_12_L
797		U_grid_L3_harmonic_amplitudes_12_H
798	float	U_grid_L3_harmonic_amplitudes_13_L
799		U_grid_L3_harmonic_amplitudes_13_H
800	float	U_grid_L3_harmonic_amplitudes_14_L
801		U_grid_L3_harmonic_amplitudes_14_H
802	float	U_grid_L3_harmonic_amplitudes_15_L
803		U_grid_L3_harmonic_amplitudes_15_H
804	float	U_grid_L3_harmonic_amplitudes_16_L
805		U_grid_L3_harmonic_amplitudes_16_H
806	float	U_grid_L3_harmonic_amplitudes_17_L
807		U_grid_L3_harmonic_amplitudes_17_H
808	float	U_grid_L3_harmonic_amplitudes_18_L
809		U_grid_L3_harmonic_amplitudes_18_H
810	float	U_grid_L3_harmonic_amplitudes_19_L
811		U_grid_L3_harmonic_amplitudes_19_H
812	float	U_grid_L3_harmonic_amplitudes_20_L
813		U_grid_L3_harmonic_amplitudes_20_H
814	float	U_grid_L3_harmonic_amplitudes_21_L
815		U_grid_L3_harmonic_amplitudes_21_H
816	float	U_grid_L3_harmonic_amplitudes_22_L
817		U_grid_L3_harmonic_amplitudes_22_H
818	float	U_grid_L3_harmonic_amplitudes_23_L
819		U_grid_L3_harmonic_amplitudes_23_H
820	float	U_grid_L3_harmonic_amplitudes_24_L
821		U_grid_L3_harmonic_amplitudes_24_H
822	float	U_grid_L3_harmonic_amplitudes_25_L
823		U_grid_L3_harmonic_amplitudes_25_H
824	float	I_grid_L1_harmonic_THD_00_L
825		I_grid_L1_harmonic_THD_00_H
826	float	I_grid_L1_harmonic_THD_01_L
827		I_grid_L1_harmonic_THD_01_H
828	float	I_grid_L1_harmonic_THD_02_L
829		I_grid_L1_harmonic_THD_02_H
830	float	I_grid_L1_harmonic_THD_03_L
831		I_grid_L1_harmonic_THD_03_H
832	float	I_grid_L1_harmonic_THD_04_L
833		I_grid_L1_harmonic_THD_04_H
834	float	I_grid_L1_harmonic_THD_05_L
835		I_grid_L1_harmonic_THD_05_H
836	float	I_grid_L1_harmonic_THD_06_L
837		I_grid_L1_harmonic_THD_06_H
838	float	I_grid_L1_harmonic_THD_07_L
839		I_grid_L1_harmonic_THD_07_H
840	float	I_grid_L1_harmonic_THD_08_L
841		I_grid_L1_harmonic_THD_08_H
842	float	I_grid_L1_harmonic_THD_09_L
843		I_grid_L1_harmonic_THD_09_H
844	float	I_grid_L1_harmonic_THD_10_L
845		I_grid_L1_harmonic_THD_10_H
846	float	I_grid_L1_harmonic_THD_11_L
847		I_grid_L1_harmonic_THD_11_H
848	float	I_grid_L1_harmonic_THD_12_L
849		I_grid_L1_harmonic_THD_12_H
850	float	I_grid_L1_harmonic_THD_13_L
851		I_grid_L1_harmonic_THD_13_H
852	float	I_grid_L1_harmonic_THD_14_L
853		I_grid_L1_harmonic_THD_14_H
854	float	I_grid_L1_harmonic_THD_15_L
855		I_grid_L1_harmonic_THD_15_H
856	float	I_grid_L1_harmonic_THD_16_L
857		I_grid_L1_harmonic_THD_16_H
858	float	I_grid_L1_harmonic_THD_17_L
859		I_grid_L1_harmonic_THD_17_H
860	float	I_grid_L1_harmonic_THD_18_L
861		I_grid_L1_harmonic_THD_18_H
862	float	I_grid_L1_harmonic_THD_19_L
863		I_grid_L1_harmonic_THD_19_H
864	float	I_grid_L1_harmonic_THD_20_L
865		I_grid_L1_harmonic_THD_20_H
866	float	I_grid_L1_harmonic_THD_21_L
567		I_grid_L1_harmonic_THD_21_H
868	float	I_grid_L1_harmonic_THD_22_L
869		I_grid_L1_harmonic_THD_22_H
870	float	I_grid_L1_harmonic_THD_23_L
871		I_grid_L1_harmonic_THD_23_H
872	float	I_grid_L1_harmonic_THD_24_L
873		I_grid_L1_harmonic_THD_24_H
874	float	I_grid_L1_harmonic_THD_25_L
875		I_grid_L1_harmonic_THD_25_H
876	float	I_grid_L2_harmonic_THD_00_L
877		I_grid_L2_harmonic_THD_00_H
878	float	I_grid_L2_harmonic_THD_01_L
879		I_grid_L2_harmonic_THD_01_H
880	float	I_grid_L2_harmonic_THD_02_L
881		I_grid_L2_harmonic_THD_02_H
882	float	I_grid_L2_harmonic_THD_03_L
883		I_grid_L2_harmonic_THD_03_H
884	float	I_grid_L2_harmonic_THD_04_L
885		I_grid_L2_harmonic_THD_04_H
886	float	I_grid_L2_harmonic_THD_05_L
887		I_grid_L2_harmonic_THD_05_H
888	float	I_grid_L2_harmonic_THD_06_L
889		I_grid_L2_harmonic_THD_06_H
890	float	I_grid_L2_harmonic_THD_07_L
891		I_grid_L2_harmonic_THD_07_H
892	float	I_grid_L2_harmonic_THD_08_L
893		I_grid_L2_harmonic_THD_08_H
894	float	I_grid_L2_harmonic_THD_09_L
895		I_grid_L2_harmonic_THD_09_H
896	float	I_grid_L2_harmonic_THD_10_L
897		I_grid_L2_harmonic_THD_10_H
898	float	I_grid_L2_harmonic_THD_11_L
899		I_grid_L2_harmonic_THD_11_H
900	float	I_grid_L2_harmonic_THD_12_L
901		I_grid_L2_harmonic_THD_12_H
802	float	I_grid_L2_harmonic_THD_13_L
903		I_grid_L2_harmonic_THD_13_H
904	float	I_grid_L2_harmonic_THD_14_L
905		I_grid_L2_harmonic_THD_14_H
906	float	I_grid_L2_harmonic_THD_15_L
907		I_grid_L2_harmonic_THD_15_H
908	float	I_grid_L2_harmonic_THD_16_L
909		I_grid_L2_harmonic_THD_16_H
910	float	I_grid_L2_harmonic_THD_17_L
911		I_grid_L2_harmonic_THD_17_H
912	float	I_grid_L2_harmonic_THD_18_L
913		I_grid_L2_harmonic_THD_18_H
914	float	I_grid_L2_harmonic_THD_19_L
915		I_grid_L2_harmonic_THD_19_H
916	float	I_grid_L2_harmonic_THD_20_L
917		I_grid_L2_harmonic_THD_20_H
918	float	I_grid_L2_harmonic_THD_21_L
919		I_grid_L2_harmonic_THD_21_H
920	float	I_grid_L2_harmonic_THD_22_L
921		I_grid_L2_harmonic_THD_22_H
922	float	I_grid_L2_harmonic_THD_23_L
923		I_grid_L2_harmonic_THD_23_H
924	float	I_grid_L2_harmonic_THD_24_L
925		I_grid_L2_harmonic_THD_24_H
926	float	I_grid_L2_harmonic_THD_25_L
927		I_grid_L2_harmonic_THD_25_H
928	float	I_grid_L3_harmonic_THD_00_L
929		I_grid_L3_harmonic_THD_00_H
930	float	I_grid_L3_harmonic_THD_01_L
931		I_grid_L3_harmonic_THD_01_H
932	float	I_grid_L3_harmonic_THD_02_L
933		I_grid_L3_harmonic_THD_02_H
934	float	I_grid_L3_harmonic_THD_03_L
935		I_grid_L3_harmonic_THD_03_H
936	float	I_grid_L3_harmonic_THD_04_L
937		I_grid_L3_harmonic_THD_04_H
938	float	I_grid_L3_harmonic_THD_05_L
939		I_grid_L3_harmonic_THD_05_H
940	float	I_grid_L3_harmonic_THD_06_L
941		I_grid_L3_harmonic_THD_06_H
942	float	I_grid_L3_harmonic_THD_07_L
943		I_grid_L3_harmonic_THD_07_H
944	float	I_grid_L3_harmonic_THD_08_L
945		I_grid_L3_harmonic_THD_08_H
946	float	I_grid_L3_harmonic_THD_09_L
947		I_grid_L3_harmonic_THD_09_H
948	float	I_grid_L3_harmonic_THD_10_L
949		I_grid_L3_harmonic_THD_10_H
950	float	I_grid_L3_harmonic_THD_11_L
951		I_grid_L3_harmonic_THD_11_H
952	float	I_grid_L3_harmonic_THD_12_L
953		I_grid_L3_harmonic_THD_12_H
954	float	I_grid_L3_harmonic_THD_13_L
955		I_grid_L3_harmonic_THD_13_H
956	float	I_grid_L3_harmonic_THD_14_L
957		I_grid_L3_harmonic_THD_14_H
958	float	I_grid_L3_harmonic_THD_15_L
959		I_grid_L3_harmonic_THD_15_H
960	float	I_grid_L3_harmonic_THD_16_L
961		I_grid_L3_harmonic_THD_16_H
962	float	I_grid_L3_harmonic_THD_17_L
963		I_grid_L3_harmonic_THD_17_H
964	float	I_grid_L3_harmonic_THD_18_L
965		I_grid_L3_harmonic_THD_18_H
966	float	I_grid_L3_harmonic_THD_19_L
967		I_grid_L3_harmonic_THD_19_H
968	float	I_grid_L3_harmonic_THD_20_L
969		I_grid_L3_harmonic_THD_20_H
970	float	I_grid_L3_harmonic_THD_21_L
971		I_grid_L3_harmonic_THD_21_H
972	float	I_grid_L3_harmonic_THD_22_L
973		I_grid_L3_harmonic_THD_22_H
974	float	I_grid_L3_harmonic_THD_23_L
975		I_grid_L3_harmonic_THD_23_H
976	float	I_grid_L3_harmonic_THD_24_L
977		I_grid_L3_harmonic_THD_24_H
978	float	I_grid_L3_harmonic_THD_25_L
979		I_grid_L3_harmonic_THD_25_H
980	float	U_grid_L1_harmonic_THD_00_L
981		U_grid_L1_harmonic_THD_00_H
982	float	U_grid_L1_harmonic_THD_01_L
983		U_grid_L1_harmonic_THD_01_H
984	float	U_grid_L1_harmonic_THD_02_L
985		U_grid_L1_harmonic_THD_02_H
986	float	U_grid_L1_harmonic_THD_03_L
987		U_grid_L1_harmonic_THD_03_H
988	float	U_grid_L1_harmonic_THD_04_L
989		U_grid_L1_harmonic_THD_04_H
990	float	U_grid_L1_harmonic_THD_05_L
991		U_grid_L1_harmonic_THD_05_H
992	float	U_grid_L1_harmonic_THD_06_L
993		U_grid_L1_harmonic_THD_06_H
994	float	U_grid_L1_harmonic_THD_07_L
995		U_grid_L1_harmonic_THD_07_H
996	float	U_grid_L1_harmonic_THD_08_L
997		U_grid_L1_harmonic_THD_08_H
998	float	U_grid_L1_harmonic_THD_09_L
999		U_grid_L1_harmonic_THD_09_H
1000	float	U_grid_L1_harmonic_THD_10_L
1001		U_grid_L1_harmonic_THD_10_H
1002	float	U_grid_L1_harmonic_THD_11_L
1003		U_grid_L1_harmonic_THD_11_H
1004	float	U_grid_L1_harmonic_THD_12_L
1005		U_grid_L1_harmonic_THD_12_H
1006	float	U_grid_L1_harmonic_THD_13_L
1007		U_grid_L1_harmonic_THD_13_H
1008	float	U_grid_L1_harmonic_THD_14_L
1009		U_grid_L1_harmonic_THD_14_H
1010	float	U_grid_L1_harmonic_THD_15_L
1011		U_grid_L1_harmonic_THD_15_H
1012	float	U_grid_L1_harmonic_THD_16_L
1013		U_grid_L1_harmonic_THD_16_H
1014	float	U_grid_L1_harmonic_THD_17_L
1015		U_grid_L1_harmonic_THD_17_H
1016	float	U_grid_L1_harmonic_THD_18_L
1017		U_grid_L1_harmonic_THD_18_H
1018	float	U_grid_L1_harmonic_THD_19_L
1019		U_grid_L1_harmonic_THD_19_H
1020	float	U_grid_L1_harmonic_THD_20_L
1021		U_grid_L1_harmonic_THD_20_H
1022	float	U_grid_L1_harmonic_THD_21_L
1023		U_grid_L1_harmonic_THD_21_H
1024	float	U_grid_L1_harmonic_THD_22_L
1025		U_grid_L1_harmonic_THD_22_H
1026	float	U_grid_L1_harmonic_THD_23_L
1027		U_grid_L1_harmonic_THD_23_H
1028	float	U_grid_L1_harmonic_THD_24_L
1029		U_grid_L1_harmonic_THD_24_H
1030	float	U_grid_L1_harmonic_THD_25_L
1031		U_grid_L1_harmonic_THD_25_H
1032	float	U_grid_L2_harmonic_THD_00_L
1033		U_grid_L2_harmonic_THD_00_H
1034	float	U_grid_L2_harmonic_THD_01_L
1035		U_grid_L2_harmonic_THD_01_H
1036	float	U_grid_L2_harmonic_THD_02_L
1037		U_grid_L2_harmonic_THD_02_H
1038	float	U_grid_L2_harmonic_THD_03_L
1039		U_grid_L2_harmonic_THD_03_H
1040	float	U_grid_L2_harmonic_THD_04_L
1041		U_grid_L2_harmonic_THD_04_H
1042	float	U_grid_L2_harmonic_THD_05_L
1043		U_grid_L2_harmonic_THD_05_H
1044	float	U_grid_L2_harmonic_THD_06_L
1045		U_grid_L2_harmonic_THD_06_H
1046	float	U_grid_L2_harmonic_THD_07_L
1047		U_grid_L2_harmonic_THD_07_H
1048	float	U_grid_L2_harmonic_THD_08_L
1049		U_grid_L2_harmonic_THD_08_H
1050	float	U_grid_L2_harmonic_THD_09_L
1051		U_grid_L2_harmonic_THD_09_H
1052	float	U_grid_L2_harmonic_THD_10_L
1053		U_grid_L2_harmonic_THD_10_H
1054	float	U_grid_L2_harmonic_THD_11_L
1055		U_grid_L2_harmonic_THD_11_H
1056	float	U_grid_L2_harmonic_THD_12_L
1057		U_grid_L2_harmonic_THD_12_H
1058	float	U_grid_L2_harmonic_THD_13_L
1059		U_grid_L2_harmonic_THD_13_H
1060	float	U_grid_L2_harmonic_THD_14_L
1061		U_grid_L2_harmonic_THD_14_H
1062	float	U_grid_L2_harmonic_THD_15_L
1063		U_grid_L2_harmonic_THD_15_H
1064	float	U_grid_L2_harmonic_THD_16_L
1065		U_grid_L2_harmonic_THD_16_H
1066	float	U_grid_L2_harmonic_THD_17_L
1067		U_grid_L2_harmonic_THD_17_H
1068	float	U_grid_L2_harmonic_THD_18_L
1069		U_grid_L2_harmonic_THD_18_H
1070	float	U_grid_L2_harmonic_THD_19_L
1071		U_grid_L2_harmonic_THD_19_H
1072	float	U_grid_L2_harmonic_THD_20_L
1073		U_grid_L2_harmonic_THD_20_H
1074	float	U_grid_L2_harmonic_THD_21_L
1075		U_grid_L2_harmonic_THD_21_H
1076	float	U_grid_L2_harmonic_THD_22_L
1077		U_grid_L2_harmonic_THD_22_H
1078	float	U_grid_L2_harmonic_THD_23_L
1079		U_grid_L2_harmonic_THD_23_H
1080	float	U_grid_L2_harmonic_THD_24_L
1081		U_grid_L2_harmonic_THD_24_H
1082	float	U_grid_L2_harmonic_THD_25_L
1083		U_grid_L2_harmonic_THD_25_H
1084	float	U_grid_L3_harmonic_THD_00_L
1085		U_grid_L3_harmonic_THD_00_H
1086	float	U_grid_L3_harmonic_THD_01_L
1087		U_grid_L3_harmonic_THD_01_H
1088	float	U_grid_L3_harmonic_THD_02_L
1089		U_grid_L3_harmonic_THD_02_H
1090	float	U_grid_L3_harmonic_THD_03_L
1091		U_grid_L3_harmonic_THD_03_H
1092	float	U_grid_L3_harmonic_THD_04_L
1093		U_grid_L3_harmonic_THD_04_H
1094	float	U_grid_L3_harmonic_THD_05_L
1095		U_grid_L3_harmonic_THD_05_H
1096	float	U_grid_L3_harmonic_THD_06_L
1097		U_grid_L3_harmonic_THD_06_H
1098	float	U_grid_L3_harmonic_THD_07_L
1099		U_grid_L3_harmonic_THD_07_H
1100	float	U_grid_L3_harmonic_THD_08_L
1101		U_grid_L3_harmonic_THD_08_H
1102	float	U_grid_L3_harmonic_THD_09_L
1103		U_grid_L3_harmonic_THD_09_H
1104	float	U_grid_L3_harmonic_THD_10_L
1105		U_grid_L3_harmonic_THD_10_H
1106	float	U_grid_L3_harmonic_THD_11_L
1107		U_grid_L3_harmonic_THD_11_H
1108	float	U_grid_L3_harmonic_THD_12_L
1109		U_grid_L3_harmonic_THD_12_H
1110	float	U_grid_L3_harmonic_THD_13_L
1111		U_grid_L3_harmonic_THD_13_H
1112	float	U_grid_L3_harmonic_THD_14_L
1113		U_grid_L3_harmonic_THD_14_H
1114	float	U_grid_L3_harmonic_THD_15_L
1115		U_grid_L3_harmonic_THD_15_H
1116	float	U_grid_L3_harmonic_THD_16_L
1117		U_grid_L3_harmonic_THD_16_H
1118	float	U_grid_L3_harmonic_THD_17_L
1119		U_grid_L3_harmonic_THD_17_H
1120	float	U_grid_L3_harmonic_THD_18_L
1121		U_grid_L3_harmonic_THD_18_H
1122	float	U_grid_L3_harmonic_THD_19_L
1123		U_grid_L3_harmonic_THD_19_H
1124	float	U_grid_L3_harmonic_THD_20_L
1125		U_grid_L3_harmonic_THD_20_H
1126	float	U_grid_L3_harmonic_THD_21_L
1127		U_grid_L3_harmonic_THD_21_H
1128	float	U_grid_L3_harmonic_THD_22_L
1139		U_grid_L3_harmonic_THD_22_H
1130	float	U_grid_L3_harmonic_THD_23_L
1131		U_grid_L3_harmonic_THD_23_H
1132	float	U_grid_L3_harmonic_THD_24_L
1133		U_grid_L3_harmonic_THD_24_H
1134	float	U_grid_L3_harmonic_THD_25_L
1135		U_grid_L3_harmonic_THD_25_H

Holding registers
0-127		FatFS_request [ 128 ]

128	u32	H_odd_a
			0x0001 – res
			0x0002 – harm3
			0x0004 – harm49

130	u32	H_odd_b	jw
132	u32	H_odd_c	jw
134	u32	H_even_a
			0x0001 – harm2
			0x0002 – harm4
136		H_even_b	jw
138		H_even_c	jw
140	3F coefficients	Q_set
		float a,b,c	przesuniecie od zera kompensacji mocy biernej
146	u32	control_bits
		0x0001	Scope_snapshot	1;
		0x0002	save_to_FLASH	1;
		0x0004	SD_save_H_Settings	1;
		0x0008	SD_save_Settings	1;
		0x0010	CPU_reset	1;
		0x0020	rsvd
		0x0040
		0x0080
		0x0100
		0x0200
		0x0400
		0x0800
		0x1000
		0x2000
		0x4000
		0x8000
147		control_bits_H
		0x0001	Modbus_FatFS_repeat	1;
		0x0002	ONOFF_override	1;
		0x0004	ONOFF	1;
		0x0008	enable_Q_comp_a	1;
		0x0010	enable_Q_comp_b	1;
		0x0020	enable_Q_comp_c	1;
		0x0040	enable_P_sym	1;
		0x0080	enable_H_comp	1;
		0x0100	version_Q_comp_a	1;
		0x0200	version_Q_comp_b	1;
		0x0400	version_Q_comp_c	1;
		0x0800	version_P_sym	1;
		0x1000	rsvd
		0x2000
		0x4000
		0x8000

148	float	tangens_range_a_H
149
150	float	tangens_range_b_H
151
152	float	tangens_range_c_H
153
154	float	tangens_range_a_L
155
156	float	tangens_range_b_L
157
158	float	tangens_range_c_L
159

160	TIME	RTC_new_time

163		rsvd